|  |  | ## Contractor Design Clarification / Variation Request (C-DCVR) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| # Project: | # Utility Service Extension to Aircraft Parts Storage – FTW 336A |  | # DU Job No.: | # J101394 to 397 |

| Contractor Request. Reference: (Dwg. / Spec.); DCVR 4 and e-mails; DCVR #:; 16; Subcontractor #: (optional). |
| --- |
| Please see below. Based on the response we received from F&H: we have installed the steam meter piping assembly exactly as specified. However, from what I have understood, Doyon wants us to cut in flanged spools for the steam meter and flow conditioner (which will simply be a piece of plate with a hole in it) because they will not be available under this contract: I was (and still am) after confirmation of the dimensions of these spools that we are going to build. It is important that we get this dead-on as we have a hard bypass spool that will not allow for much, if any change in tolerance and, because the incorrect meter we originally received was different from that listed in the Prowirl manual (though not by much) is why I am asking the question. Steam meter: 7.88” flange to flange Flow conditioner: 0.27” thick |  |  |  |  |  |  |  |  |
| Company: | TAR/TBI Construction | Signature: | Kris Manke |  |  | Date: |  | RFP requested? Yes No |
| Response requested no later than 5:00 p.m. on (date): |  |  |  |  | Allow minimum 4 working days. Contractor must make verbal request for an expedited response. |  |  |  |

| Architect/Engineer Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| The above dimensions are correct per the Endress+Hauser Technical Information document for the Prowirl 73F meter. Please note that the documentation states a tolerance of ±0.10” for the flange-to-flange length, meaning that actual length may vary from 7.78” to 7.98”. No tolerance figures are given for the flow conditioner thickness. |  |  |  |  |  |  |
| Company: | Fosdick & Hilmer, Inc. | Signature: | Luke Grubbs | Date: | 12/2/2010 | RFP warranted? Yes No |

| Doyon Utilities Response Agree w/ Architect/Engineer. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| #### APPROVED DISAPPROVED |  | #### Signature: |  | #### Date: |  |  |
| #### RFP issued? No Yes RFP#: |  |  |  |  |  |  |

THIS IS NOT AUTHORIZATION TO PROCEED WITH WORK INVOLVING ADDITIONAL COST AND/OR TIME.
Contractor must notify Doyon Utilities if any information provided herein may add to the Contract cost and/or time.