|  |  | ## Contractor Design Clarification / Variation Request (C-DCVR) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| # Project: | # Utility Service Extension to Aircraft Parts Storage – FTW 336A |  | # DU Job No.: | # J101394 to 397 |

| Contractor Request. Reference: (Dwg. / Spec.); 336A Utility Ext. PC-G693.3.1; DCVR #:; 17; Subcontractor #: (optional). |
| --- |
| We believe we’ve received the wrong device for an outdoor app. According to the print, TT-H6-3-3-VLT requires a 2 wire device, and we received a 4 wire device. We believe we’ve received the wrong device for TT/MT G6-9-3-VLT. Device received is p/n TE500AS12GS003 and is a TT only. |  |  |  |  |  |  |  |  |
| Company: | Fullford Electric Inc. | Signature: | Kris Manke |  |  | Date: | 12-2-10 | RFP requested? Yes No |
| Response requested no later than 5:00 p.m. on (date): |  |  |  |  | Allow minimum 4 working days. Contractor must make verbal request for an expedited response. |  |  |  |

| Architect/Engineer Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Clarifications: - TT-H6-3-3-VLT is a 2-wire temperature transmitter (MFG: Greystone, P/N: TE500AS12GS003) for wall-mounting within vault H6-3-3. - TT-G6-9-3-OA is a 2-wire outdoor temperature transmitter (MFG: Greystone, P/N: TE500F121A10X) for mounting external to vault G6-9-3. - TT/MT-G6-9-3-VLT is a 4-wire combination temperature/humidity transmitter (MFG: Greystone, P/N: RH310A03C1A6) for wall-mounting within vault G6-9-3. |  |  |  |  |  |  |
| Company: | Fosdick & Hilmer, Inc. | Signature: | Luke Grubbs | Date: | 12/9/2010 | RFP warranted? Yes No |

| Doyon Utilities Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Agreed. |  |  |  |  |  |  |
| #### APPROVED DISAPPROVED |  | #### Signature: | Wily F. Splain | #### Date: | #### 12/13/10 |  |
| #### RFP issued? No Yes RFP#: |  |  |  |  |  |  |

THIS IS NOT AUTHORIZATION TO PROCEED WITH WORK INVOLVING ADDITIONAL COST AND/OR TIME.
Contractor must notify Doyon Utilities if any information provided herein may add to the Contract cost and/or time.