|  |  | ## Contractor Design Clarification / Variation Request (C-DCVR) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| # Project: | # Utility Service Extension to Aircraft Parts Storage – FTW 336A |  | # DU Job No.: | # J101394 to 397 |

| Contractor Request. Reference: (Dwg. / Spec.); 336A Utility Ext. PC-G693.3.1; DCVR #:; 17; Subcontractor #: (optional). |
| --- |
| We believe we’ve received the wrong device for an outdoor app. According to the print, TT-H6-3-3-VLT requires a 2 wire device, and we received a 4 wire device. We believe we’ve received the wrong device for TT/MT G6-9-3-VLT. Device received is p/n TE500AS12GS003 and is a TT only. All of the below devices were mislabeled in the boxes which caused all of the problems, once we received this answer we brought all of the boxes in my office and re-labeled everything, still have one unit that does not match what you guys say here please see below. |  |  |  |  |  |  |  |  |
| Company: | Fullford Electric Inc. | Signature: | Kris Manke |  |  | Date: | 12-2-10 | RFP requested? Yes No |
| Response requested no later than 5:00 p.m. on (date): |  |  |  |  | Allow minimum 4 working days. Contractor must make verbal request for an expedited response. |  |  |  |

| Architect/Engineer Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Clarifications: - TT-H6-3-3-VLT is a 2-wire temperature transmitter (MFG: Greystone, P/N: TE500AS12GS003) for wall-mounting within vault H6-3-3. - TT-G6-9-3-OA is a 2-wire outdoor temperature transmitter (MFG: Greystone, P/N: TE500F121A10X) for mounting external to vault G6-9-3. The P/N we have for this unit is TE500F12GS002. - TT/MT-G6-9-3-VLT is a 4-wire combination temperature/humidity transmitter (MFG: Greystone, P/N: RH310A03C1A6) for wall-mounting within vault G6-9-3. |  |  |  |  |  |  |
| Company: | Fosdick & Hilmer, Inc. | Signature: | Luke Grubbs | Date: | 12/9/2010 | RFP warranted? Yes No |

| Doyon Utilities Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| #### APPROVED DISAPPROVED |  | #### Signature: | Wily F. Splain | #### Date: | #### 12/13/10 |  |
| #### RFP issued? No Yes RFP#: |  |  |  |  |  |  |

THIS IS NOT AUTHORIZATION TO PROCEED WITH WORK INVOLVING ADDITIONAL COST AND/OR TIME.
Contractor must notify Doyon Utilities if any information provided herein may add to the Contract cost and/or time.