|  |  | ## Contractor Design Clarification / Variation Request (C-DCVR) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| # Project: | # Utilities Extension to Aircraft Parts Storage - FTW 336A |  | # DU Job No.: | # J101534, 5 & 7 |

| Contractor Request. Reference: (Dwg. / Spec.); Drawing E-04 & E-06 (Circulation Pump Changes); DCVR #:; 14; Subcontractor #: (optional). |
| --- |
| This DCVR is issued as a clarification for the contractor regarding the circulating pump P-G693-DCW. Drawing E-04 currently shows P-G693-DCW requiring a 5 HP, 208 V, 3 phase electric motor feed. This pump and motor has been modified and the actual pump furnished by Doyon Utilities will be a 1/6 HP, 120 V, 1 phase motor. |  |  |  |  |  |  |  |  |
| Company: | F&H | Signature: | Eric Erpenbeck |  |  | Date: | 9/10/10 | RFP requested? Yes No |
| Response requested no later than 5:00 p.m. on (date): |  |  |  |  | Allow minimum 4 working days. Contractor must make verbal request for an expedited response. |  |  |  |

| Architect/Engineer Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| See revised E-04 and E-06 drawings (attached) for the necessary changes to the electric service feed to pump P-G693-DCW. Provide a RFP for these changes. |  |  |  |  |  |  |
| Company: | Fosdick & Hilmer, Inc. | Signature: | Luke Grubbs | Date: | 9/10/2010 | RFP warranted? Yes No |

| Doyon Utilities Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Agreed. Please propose implementation of said changes. Thank you. |  |  |  |  |  |  |
| #### APPROVED DISAPPROVED |  | #### Signature: | Wily F. Splain | #### Date: | #### 9/28/2010 |  |
| #### RFP issued? No Yes RFP#: |  |  |  |  |  |  |

THIS IS NOT AUTHORIZATION TO PROCEED WITH WORK INVOLVING ADDITIONAL COST AND/OR TIME.
Contractor must notify Doyon Utilities if any information provided herein may add to the Contract cost and/or time.