|  |  | ## Contractor Design Clarification / Variation Request (C-DCVR) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| # Project: | # Utility Service Extension to Aircraft Parts Storage – FTW 336A |  | # DU Job No.: | # J101394 to 397 |

| Contractor Request. Reference: (Dwg. / Spec.); Throughout the drawings; DCVR #:; 3; Subcontractor #: (optional); 2. |
| --- |
| We propose to utilize the attached configuration for the steam traps and sparge tubes, which consists of a long radius butt weld 90 pointing into the adjoining main line pipe with the direction of flow. We have had numerous projects in the past where we had to cut out sparge tube assemblies constructed per HDS-202 standard detail after the 1/8” perforate holes plug up over time. |  |  |  |  |  |  |  |  |
| Company: | TAR/TBI Construction | Signature: | Kris Manke |  |  | Date: | 8-5-10 | RFP requested? Yes No |
| Response requested no later than 5:00 p.m. on (date): |  |  |  |  | Allow minimum 4 working days. Contractor must make verbal request for an expedited response. |  |  |  |

| Architect/Engineer Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| The intent of the condensate sparger is to reduce the adverse effects of MPR flashing, water hammering, and cavitation induced impingement wear on the walls of the PCR piping in the area of the trap station connection. The submitted alternate is an unrestricted trap discharge into the PCR piping and will not accomplish the design intent of the condensate sparger. We would be happy to consider other options you may propose that meets the above design criteria. At this point, the sparger assembly from the drip leg steam trap station shall be installed per UES-DD-H002. Use of detail HDS-202 on the DU website is not to be followed and was not referenced in the construction documents. |  |  |  |  |  |  |
| Company: | Fosdick & Hilmer, Inc. | Signature: | Norman Miller | Date: | 10 Aug 10 | RFP warranted? Yes No |

| Doyon Utilities Response |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| #### APPROVED √ DISAPPROVED |  | #### Signature: |  | #### Date: |  |  |
| #### RFP issued? No Yes RFP#: |  |  |  |  |  |  |

THIS IS NOT AUTHORIZATION TO PROCEED WITH WORK INVOLVING ADDITIONAL COST AND/OR TIME.
Contractor must notify Doyon Utilities if any information provided herein may add to the Contract cost and/or time.