## FTW336A Lateral (30 Oct 09)
Project Cost Estimating Worksheet
Fort Wainwright FTW336A | Utility Service Lateral from Existing Mains to Aircraft Parts Storage
Item | Year Inst | Quantity |  | Unit Cost | RCN | Contractors Mark-ups % |  |  |  |  | Contractors Mark-ups $ |  |  |  |  | RCN (Total Installed) | Engineering Services % |  |  |  | Engineering Services $'s |  |  |  | RCN Total w. Engineering) | Design Life | RYN (Repl. Year New) | RDL (Repl. Design Life) | Comments
Service utilidor w/ HDS & WDS ---- WWCS direct buried next to new utilidor | [5 empty] | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit |  | Studies & Pre-Design | Design | Services During Construction(3%) & Commissioning (2%) | Fee's on Studies & Design | Studies & Pre-Design | Design | Services During Construction | Fee's on Studies & Design |  |  | CY
Site Preparation & Access
site preparation, overburden excavation and removal, sedimentation control | 2010 | 200 | LF | 50 | 10000 | 5% | 2% | 5% | 12.2% | 10% | 500 | 210 | 535.5 | 1371.951 | 1261.7451 | 13879.1961 |  |  | 5% | 10% | 0 | 0 | 693.9598 | 0 | 14573.1559 | 75 |  | 75
isolation tenting, ventilation, lid removal and cribbing, isolation bulkheads, repair or replacement of broken utilidor roof panels | 2010 | 200 | LF | 25 | 5000 | 5% | 2% | 5% | 12.2% | 10% | 250 | 105 | 267.75 | 685.9755 | 630.8726 | 6939.5981 |  |  | 5% | 10% | 0 | 0 | 346.9799 | 0 | 7286.578 | 75 |  | 75
utilidor roof panel clean-up and reinstallation; backfill; finish grading; pavement repair; turf and landscape repair. | 2010 | 200 | LF | 75 | 15000 | 5% | 2% | 5% | 12.2% | 10% | 750 | 315 | 803.25 | 2057.9265 | 1892.6177 | 20818.7942 |  |  | 5% | 10% | 0 | 0 | 1040.9397 | 0 | 21859.7339 | 75 |  | 75
Asbestos Containing Material Abatement
Utilidor Steam Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Carbon steel piping, ASTM A106, seamless, standard wall; forged carbon steel fittings; forged carbon steel valves (2" and smaller); cast carbon steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed steam piping - 3" diameter | 2010 | 400 | LF | 233 | 93200 | 5% | 2% | 5% | 12.2% | 10% | 4660 | 1957.2 | 4990.86 | 12786.5833 | 11759.4643 | 129354.1077 |  |  | 5% | 10% | 0 | 0 | 6467.7054 | 0 | 135821.813 | 60 |  | 60
Utilidor Condensate Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Stainless steel piping, ASTM A312, Type 316L, schedule 10S; wrought stainless steel fittings; forged stainless steel valves (2" and smaller); cast stainless steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed condensate piping - 1½" diameter | 2010 | 400 | LF | 205 | 82000 | 5% | 2% | 5% | 12.2% | 10% | 4100 | 1722 | 4391.1 | 11249.9982 | 10346.3098 | 113809.408 |  |  | 5% | 10% | 0 | 0 | 5690.4704 | 0 | 119499.8784 | 40 |  | 40
Utilidor Water Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new support and anchor systems; new insulation and tracing; reconnect or replace service laterals as required.
Copper tubing (3" and smaller), ASTM B88, type K; cast bronze fittings, ASTM A536; cast bronze valves; mechanical couplings for roll grooved piping system.
utilidor installed water piping - 2" diameter | 2010 | 400 | LF | 63 | 25200 | 5% | 2% | 5% | 12.2% | 10% | 1260 | 529.2 | 1349.46 | 3457.3165 | 3179.5977 | 34975.5742 |  |  | 5% | 10% | 0 | 0 | 1748.7787 | 0 | 36724.3529 | 70 |  | 70
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
utilidor installed water piping - 8" diameter | 2010 | 250 | LF | 254 | 63500 | 5% | 2% | 5% | 12.2% | 10% | 3175 | 1333.5 | 3400.425 | 8711.8888 | 8012.0814 | 88132.8952 |  |  | 5% | 10% | 0 | 0 | 4406.6448 | 0 | 92539.54 | 70 |  | 70
Utilidor Rehabilitation and Repair
Repair and recondition utilidor walls, floor and removable roof panels; repair/replace utilidor insulation and waterproofing system. | 2010 | 150 | LF | 125 | 18750 | 5% | 2% | 5% | 12.2% | 10% | 937.5 | 393.75 | 1004.0625 | 2572.4081 | 2365.7721 | 26023.4927 |  |  | 5% | 10% | 0 | 0 | 1301.1746 | 0 | 27324.6673 | 75 |  | 75
Raise elevation of manhole lid where required to eliminate seasonal flooding of utilidor system. | 2010 | 4 | EA | 1750 | 7000 | 5% | 2% | 5% | 12.2% | 10% | 350 | 147 | 374.85 | 960.3657 | 883.2216 | 9715.4373 |  |  | 5% | 10% | 0 | 0 | 485.7719 | 0 | 10201.2091 | 75 |  | 75
Repair/replace utilidor ventilation system in manhole lid (where required). | 2010 | 6 | EA | 2200 | 13200 | 5% | 2% | 5% | 12.2% | 10% | 660 | 277.2 | 706.86 | 1810.9753 | 1665.5035 | 18320.5389 |  |  | 5% | 10% | 0 | 0 | 916.0269 | 0 | 19236.5658 | 75 |  | 75
Replace manhole convenience power and lighting system (where required). | 2010 | 6 | EA | 1800 | 10800 | 5% | 2% | 5% | 12.2% | 10% | 540 | 226.8 | 578.34 | 1481.7071 | 1362.6847 | 14989.5318 |  |  | 5% | 10% | 0 | 0 | 749.4766 | 0 | 15739.0084 | 25 |  | 25
Replace utilidor drainage system , sump pumps (where required) | 2010 | 0 | EA | 2600 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Replace existing access hatches with new secure (lockable) hatches. | 2010 | 6 | EA | 3065 | 18390 | 5% | 2% | 5% | 12.2% | 10% | 919.5 | 386.19 | 984.7845 | 2523.0179 | 2320.3492 | 25523.8416 |  |  | 5% | 10% | 0 | 0 | 1276.1921 | 0 | 26800.0337 | 75 |  | 75
Utilidor Replacement - Includes removal and recycling of existing concrete utilidor elements. Replacement also includes mastic damp proofing, board insulation, access hatches, vents, lighting, and sumps with submersible pumps.
8 foot long precast concrete U-sections with precast concrete lids; ACI 317, 5000 psi concrete,
Precast concrete sections - 54" by 54" | 2010 | 225 | LF | 630 | 141750 | 5% | 2% | 5% | 12.2% | 10% | 7087.5 | 2976.75 | 7590.7125 | 19447.4054 | 17885.2368 | 196737.6047 |  |  | 5% | 10% | 0 | 0 | 9836.8802 | 0 | 206574.485 | 75 |  | 75
Direct Buried Domestic Water Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
direct buried water main (DU Water Service Table March 2008) - 6" diameter | 2010 | 100 | LF | 110 | 11000 | 5% | 2% | 5% | 12.2% | 10% | 550 | 231 | 589.05 | 1509.1461 | 1387.9196 | 15267.1157 |  |  | 5% | 10% | 0 | 0 | 763.3558 | 0 | 16030.4715 | 70 |  | 70
Direct Buried Sewer Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
Gravity:
direct buried sewer piping - 8" gravity | 2010 | 400 | LF | 254 | 101600 | 5% | 2% | 5% | 12.2% | 10% | 5080 | 2133.6 | 5440.68 | 13939.0222 | 12819.3302 | 141012.6324 |  |  | 5% | 10% | 0 | 0 | 7050.6316 | 0 | 148063.264 | 70 |  | 70
Force Main:
EDS
225kva 12.4Y/7.2 kv 277/480 Volt Padmount Transformer | 2010 | 1 | ea | 8500 | 8500 | 5% | 2% | 5% | 12.2% | 10% | 425 | 178.5 | 455.175 | 1166.1583 | 1072.4833 | 11797.3167 |  |  | 5% | 10% | 0 | 0 | 589.8658 | 0 | 12387.1825 | 70 |  | 70
13-Jaw 225 Amp Meterbase w/CK Closing Device | 2010 | 1 | ea | 275 | 275 | 5% | 2% | 5% | 12.2% | 10% | 13.75 | 5.775 | 14.7263 | 37.7287 | 34.698 | 381.6779 |  |  | 5% | 10% | 0 | 0 | 19.0839 | 0 | 400.7618 | 70 |  | 70
CT Enclosure | 2010 | 1 | ea | 800 | 800 | 5% | 2% | 5% | 12.2% | 10% | 40 | 16.8 | 42.84 | 109.7561 | 100.9396 | 1110.3357 |  |  | 5% | 10% | 0 | 0 | 55.5168 | 0 | 1165.8525 | 70 |  | 70
225A Service Rated NEMA 3R Circuit Breaker | 2010 | 1 | ea | 1250 | 1250 | 5% | 2% | 5% | 12.2% | 10% | 62.5 | 26.25 | 66.9375 | 171.4939 | 157.7181 | 1734.8995 |  |  | 5% | 10% | 0 | 0 | 86.745 | 0 | 1821.6445 | 70 |  | 70
400:5 CT's | 2010 | 3 | ea | 350 | 1050 | 5% | 2% | 5% | 12.2% | 10% | 52.5 | 22.05 | 56.2275 | 144.0549 | 132.4832 | 1457.3156 |  |  | 5% | 10% | 0 | 0 | 72.8658 | 0 | 1530.1814 | 70 |  | 70
13-Jaw FM9S Meter | 2010 | 1 | ea | 220 | 220 | 5% | 2% | 5% | 12.2% | 10% | 11 | 4.62 | 11.781 | 30.1829 | 27.7584 | 305.3423 |  |  | 5% | 10% | 0 | 0 | 15.2671 | 0 | 320.6094 | 70 |  | 70
UM1-1B Pad Assembly-Concrete | 2010 | 1 | ea | 2400 | 2400 | 5% | 2% | 5% | 12.2% | 10% | 120 | 50.4 | 128.52 | 329.2682 | 302.8188 | 3331.0071 |  |  | 5% | 10% | 0 | 0 | 166.5504 | 0 | 3497.5574 | 70 |  | 70
UC1X Three Phase Primary Riser | 2010 | 1 | ea | 4700 | 4700 | 5% | 2% | 5% | 12.2% | 10% | 235 | 98.7 | 251.685 | 644.817 | 593.0202 | 6523.2222 |  |  | 5% | 10% | 0 | 0 | 326.1611 | 0 | 6849.3833 | 70 |  | 70
UM6-1 200A Load Break Elbow | 2010 | 3 | ea | 350 | 1050 | 5% | 2% | 5% | 12.2% | 10% | 52.5 | 22.05 | 56.2275 | 144.0549 | 132.4832 | 1457.3156 |  |  | 5% | 10% | 0 | 0 | 72.8658 | 0 | 1530.1814 | 70 |  | 70
1/0 15kv URD Concentric Primary Cable 133% Insulation | 2010 | 225 | FT | 8 | 1800 | 5% | 2% | 5% | 12.2% | 10% | 90 | 37.8 | 96.39 | 246.9512 | 227.1141 | 2498.2553 |  |  | 5% | 10% | 0 | 0 | 124.9128 | 0 | 2623.1681 | 70 |  | 70
UM50-P-3 3" PVC Conduit | 2010 | 110 | FT | 24 | 2640 | 5% | 2% | 5% | 12.2% | 10% | 132 | 55.44 | 141.372 | 362.1951 | 333.1007 | 3664.1078 |  |  | 5% | 10% | 0 | 0 | 183.2054 | 0 | 3847.3132 | 70 |  | 70
3" GRC Elbow | 2010 | 4 | ea | 175 | 700 | 5% | 2% | 5% | 12.2% | 10% | 35 | 14.7 | 37.485 | 96.0366 | 88.3222 | 971.5437 |  |  | 5% | 10% | 0 | 0 | 48.5772 | 0 | 1020.1209 | 70 |  | 70
UM6-6 Ground Rod Assembly | 2010 | 1 | ea | 175 | 175 | 5% | 2% | 5% | 12.2% | 10% | 8.75 | 3.675 | 9.3713 | 24.0091 | 22.0805 | 242.8859 |  |  | 5% | 10% | 0 | 0 | 12.1443 | 0 | 255.0302 | 70 |  | 70
250kcml Secondary Conductor | 2010 | 120 | FT | 7 | 840 | 5% | 2% | 5% | 12.2% | 10% | 42 | 17.64 | 44.982 | 115.2439 | 105.9866 | 1165.8525 |  |  | 5% | 10% | 0 | 0 | 58.2926 | 0 | 1224.1451 | 70 |  | 70
G3.3 25kva 12.4/7.2kv 120/208 Volt Transformer | 2010 | 3 | ea | 1250 | 3750 | 5% | 2% | 5% | 12.2% | 10% | 187.5 | 78.75 | 200.8125 | 514.4816 | 473.1544 | 5204.6985 |  |  | 5% | 10% | 0 | 0 | 260.2349 | 0 | 5464.9335 | 70 |  | 70
UM6 Three Phase Secondary Riser 3/0 XHHW2 | 2010 | 300 | FT | 5 | 1500 | 5% | 2% | 5% | 12.2% | 10% | 75 | 31.5 | 80.325 | 205.7927 | 189.2618 | 2081.8794 |  |  | 5% | 10% | 0 | 0 | 104.094 | 0 | 2185.9734 | 70 |  | 70
F2.8 Double Helix Anchor | 2010 | 1 | ea | 400 | 400 | 5% | 2% | 5% | 12.2% | 10% | 20 | 8.4 | 21.42 | 54.878 | 50.4698 | 555.1678 |  |  | 5% | 10% | 0 | 0 | 27.7584 | 0 | 582.9262 | 70 |  | 70
E2.1X Single Down Guy Heavy Duty | 2010 | 1 | ea | 350 | 350 | 5% | 2% | 5% | 12.2% | 10% | 17.5 | 7.35 | 18.7425 | 48.0183 | 44.1611 | 485.7719 |  |  | 5% | 10% | 0 | 0 | 24.2886 | 0 | 510.0605 | 70 |  | 70
1/0 ACSR Primary Conductor | 2010 | 400 | FT | 6 | 2400 | 5% | 2% | 5% | 12.2% | 10% | 120 | 50.4 | 128.52 | 329.2682 | 302.8188 | 3331.0071 |  |  | 5% | 10% | 0 | 0 | 166.5504 | 0 | 3497.5574 | 70 |  | 70
C5.31X Single Deadend Neutal on X-arm | 2010 | 1 | ea | 1050 | 1050 | 5% | 2% | 5% | 12.2% | 10% | 52.5 | 22.05 | 56.2275 | 144.0549 | 132.4832 | 1457.3156 |  |  | 5% | 10% | 0 | 0 | 72.8658 | 0 | 1530.1814 | 70 |  | 70
C1.41 Single Support Neutral on X-arm | 2010 | 1 | ea | 625 | 625 | 5% | 2% | 5% | 12.2% | 10% | 31.25 | 13.125 | 33.4688 | 85.7469 | 78.8591 | 867.4498 |  |  | 5% | 10% | 0 | 0 | 43.3725 | 0 | 910.8222 | 70 |  | 70
H1.1 Ground Rod Assembly | 2010 | 2 | ea | 175 | 350 | 5% | 2% | 5% | 12.2% | 10% | 17.5 | 7.35 | 18.7425 | 48.0183 | 44.1611 | 485.7719 |  |  | 5% | 10% | 0 | 0 | 24.2886 | 0 | 510.0605 | 70 |  | 70
P-45 45' cl 2 Wood Pole | 2010 | 2 | ea | 2600 | 5200 | 5% | 2% | 5% | 12.2% | 10% | 260 | 109.2 | 278.46 | 713.4145 | 656.1075 | 7217.182 |  |  | 5% | 10% | 0 | 0 | 360.8591 | 0 | 7578.0411 | 70 |  | 70
| 2010 | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
7-Jaw 200A Meterbase | 2010 | 1 | ea | 275 | 275 | 5% | 2% | 5% | 12.2% | 10% | 13.75 | 5.775 | 14.7263 | 37.7287 | 34.698 | 381.6779 |  |  | 5% | 10% | 0 | 0 | 19.0839 | 0 | 400.7618 | 70 |  | 70
7-Jaw 100A Meterbase | 2010 | 1 | ea | 250 | 250 | 5% | 2% | 5% | 12.2% | 10% | 12.5 | 5.25 | 13.3875 | 34.2988 | 31.5436 | 346.9799 |  |  | 5% | 10% | 0 | 0 | 17.349 | 0 | 364.3289 | 70 |  | 70
7-Jaw 200A FM16S Meter | 2010 | 2 | ea | 200 | 400 | 5% | 2% | 5% | 12.2% | 10% | 20 | 8.4 | 21.42 | 54.878 | 50.4698 | 555.1678 |  |  | 5% | 10% | 0 | 0 | 27.7584 | 0 | 582.9262 | 70 |  | 70
100 Amp Lighting Load Control Center | 2010 | 1 | ea | 3600 | 3600 | 5% | 2% | 5% | 12.2% | 10% | 180 | 75.6 | 192.78 | 493.9024 | 454.2282 | 4996.5106 |  |  | 5% | 10% | 0 | 0 | 249.8255 | 0 | 5246.3361 | 70 |  | 70
Steel Light Pole (sigle fixture) w/250 Watt HPS Light | 2010 | 4 | ea | 2700 | 10800 | 5% | 2% | 5% | 12.2% | 10% | 540 | 226.8 | 578.34 | 1481.7071 | 1362.6847 | 14989.5318 |  |  | 5% | 10% | 0 | 0 | 749.4766 | 0 | 15739.0084 | 70 |  | 70
3/4" Lighting Branch Conduit w/#10 | 2010 | 200 | FT | 8 | 1600 | 5% | 2% | 5% | 12.2% | 10% | 80 | 33.6 | 85.68 | 219.5122 | 201.8792 | 2220.6714 |  |  | 5% | 10% | 0 | 0 | 111.0336 | 0 | 2331.7049 | 70 |  | 70
Light Standard - Concrete Foundation | 2010 | 4 | ea | 1950 | 7800 | 5% | 2% | 5% | 12.2% | 10% | 390 | 163.8 | 417.69 | 1070.1218 | 984.1612 | 10825.773 |  |  | 5% | 10% | 0 | 0 | 541.2886 | 0 | 11367.0616 | 70 |  | 70
| 2010 | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Other Project Specific Items
Fire hydrant - replacement including lateral piping, tracing and insulation | 2010 | 2 | EA | 17500 | 35000 | 5% | 2% | 5% | 12.2% | 10% | 1750 | 735 | 1874.25 | 4801.8285 | 4416.1079 | 48577.1864 |  |  | 5% | 10% | 0 | 0 | 2428.8593 | 0 | 51006.0457 | 25 |  | 25
Steam Flow Meter - 3" | 2010 | 1 | EA | 7500 | 7500 | 5% | 2% | 5% | 12.2% | 10% | 375 | 157.5 | 401.625 | 1028.9633 | 946.3088 | 10409.3971 |  |  | 5% | 10% | 0 | 0 | 520.4699 | 0 | 10929.8669 | 25 |  | 25
Water Flow Meter - 2" | 2010 | 1 | EA | 2300 | 2300 | 5% | 2% | 5% | 12.2% | 10% | 115 | 48.3 | 123.165 | 315.5487 | 290.2014 | 3192.2151 |  |  | 5% | 10% | 0 | 0 | 159.6108 | 0 | 3351.8259 | 25 |  | 25
Install Concrete Access Vaults | 2010 | 2 | EA | 17000 | 34000 | 5% | 2% | 5% | 12.2% | 10% | 1700 | 714 | 1820.7 | 4664.6334 | 4289.9333 | 47189.2667 |  |  | 5% | 10% | 0 | 0 | 2359.4633 | 0 | 49548.7301 | 25 |  | 25
Total Project Cost |  |  |  |  | 761940 | [10 empty] | 1057511.4676 | [5 empty] | Total CPM & Commissioning | 52875.5734 |  | 1110387.041 |  |  | 64.8077
|  |  |  | CY#3 | CY#4 | [14 empty] | Annual Property Tax Impact |  |  |  |  | 19185.2673
Rate Base
|  |  | Tariff Impact | 7762 | 13189
CIAC
|  |  | Tariff Impact | 2169 | 4284
|  |  | Op Fee Impact | 4580 | 4488

## FTW336A Lat (15 Sep 09)
Project Cost Estimating Worksheet
Fort Wainwright FTW336A | Utility Service Lateral from Existing Mains to Aircraft Parts Storage
Item | Year Inst | Quantity |  | Unit Cost | RCN | Contractors Mark-ups % |  |  |  |  | Contractors Mark-ups $ |  |  |  |  | RCN (Total Installed) | Engineering Services % |  |  |  | Engineering Services $'s |  |  |  | RCN Total w. Engineering) | Design Life | RYN (Repl. Year New) | RDL (Repl. Design Life) | Comments
Service utilidor w/ HDS & WDS ---- WWCS direct buried next to new utilidor | [5 empty] | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit |  | Studies & Pre-Design | Design | Services During Construction(3%) & Commissioning (2%) | Fee's on Studies & Design | Studies & Pre-Design | Design | Services During Construction | Fee's on Studies & Design |  |  | CY
Site Preparation & Access
site preparation, overburden excavation and removal, sedimentation control |  | 400 | LF | 50 | 20000 | 5% | 2% | 5% | 12.2% | 10% | 1000 | 420 | 1071 | 2743.902 | 2523.4902 | 27758.3922 | 5% | 5% | 5% | 10% | 1387.9196 | 1387.9196 | 1387.9196 | 277.5839 | 32199.735 | 75 |  | 75
isolation tenting, ventilation, lid removal and cribbing, isolation bulkheads, repair or replacement of broken utilidor roof panels |  | 0 | LF | 25 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
utilidor roof panel clean-up and reinstallation; backfill; finish grading; pavement repair; turf and landscape repair. |  | 400 | LF | 75 | 30000 | 5% | 2% | 5% | 12.2% | 10% | 1500 | 630 | 1606.5 | 4115.853 | 3785.2353 | 41637.5883 | 5% | 5% | 5% | 10% | 2081.8794 | 2081.8794 | 2081.8794 | 416.3759 | 48299.6024 | 75 |  | 75
Asbestos Containing Material Abatement
asbestos pipe insulation removal and disposal in POST landfill |  | 0 | LF | 175 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
utilidor clean up & asbestos encapsulation |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Utilidor Steam Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Carbon steel piping, ASTM A106, seamless, standard wall; forged carbon steel fittings; forged carbon steel valves (2" and smaller); cast carbon steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed steam piping - 1" diameter |  | 0 | LF | 161 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 1½" diameter |  | 0 | LF | 175 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 2" diameter |  | 0 | LF | 191 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 3" diameter |  | 400 | LF | 233 | 93200 | 5% | 2% | 5% | 12.2% | 10% | 4660 | 1957.2 | 4990.86 | 12786.5833 | 11759.4643 | 129354.1077 | 5% | 5% | 5% | 10% | 6467.7054 | 6467.7054 | 6467.7054 | 1293.5411 | 150050.7649 | 60 |  | 60
utilidor installed steam piping - 4" diameter |  | 0 | LF | 292 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 6" diameter |  | 0 | LF | 320 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 8" diameter |  | 0 | LF | 374 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 10" diameter |  | 0 | LF | 447 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 12" diameter |  | 0 | LF | 505 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 14" diameter |  | 0 | LF | 547 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 16" diameter |  | 0 | LF | 588 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 18" diameter |  | 0 | LF | 691 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 20" diameter |  | 0 | LF | 785 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 24" diameter |  | 0 | LF | 891 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
Utilidor Condensate Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Stainless steel piping, ASTM A312, Type 316L, schedule 10S; wrought stainless steel fittings; forged stainless steel valves (2" and smaller); cast stainless steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed condensate piping - ½" diameter |  | 0 | LF | 190 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - ¾" diameter |  | 0 | LF | 187 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 1" diameter |  | 0 | LF | 198 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 1½" diameter |  | 400 | LF | 205 | 82000 | 5% | 2% | 5% | 12.2% | 10% | 4100 | 1722 | 4391.1 | 11249.9982 | 10346.3098 | 113809.408 | 5% | 5% | 5% | 10% | 5690.4704 | 5690.4704 | 5690.4704 | 1138.0941 | 132018.9133 | 40 |  | 40
utilidor installed condensate piping - 2" diameter |  | 0 | LF | 217 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 3" diameter |  | 0 | LF | 230 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 4" diameter |  | 0 | LF | 250 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 6" diameter |  | 0 | LF | 364 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 8" diameter |  | 0 | LF | 350 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 10" diameter |  | 0 | LF | 401 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 12" diameter |  | 0 | LF | 423 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
Utilidor Water Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new support and anchor systems; new insulation and tracing; reconnect or replace service laterals as required.
Copper tubing (3" and smaller), ASTM B88, type K; cast bronze fittings, ASTM A536; cast bronze valves; mechanical couplings for roll grooved piping system.
utilidor installed water piping - 1½" diameter |  | 0 | LF | 54 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 2" diameter |  | 0 | LF | 63 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 2½" diameter |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 3" diameter |  | 0 | LF | 94 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
utilidor installed water piping - 4" diameter |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 6" diameter |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 8" diameter |  | 400 | LF | 254 | 101600 | 5% | 2% | 5% | 12.2% | 10% | 5080 | 2133.6 | 5440.68 | 13939.0222 | 12819.3302 | 141012.6324 | 5% | 5% | 5% | 10% | 7050.6316 | 7050.6316 | 7050.6316 | 1410.1263 | 163574.6536 | 70 |  | 70
utilidor installed water piping - 10" diameter |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 14" diameter |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 16" diameter |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 18" diameter |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 20" diameter |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Utilidor Sewer Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new support and anchor systems; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
Gravity:
utilidor installed sewer piping - 3" gravity |  | 0 | LF | 196 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 4" gravity |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 6" gravity |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 8" gravity |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 10" gravity |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 12" gravity |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 14" gravity |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 16" gravity |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 18" gravity |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 20" gravity |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 24" gravity |  | 0 | LF | 476 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Force Main:
utilidor installed force main - 4" diameter |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 6" diameter |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 8" diameter |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 10" diameter |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 14" diameter |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 16" diameter |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 18" diameter |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 20" diameter |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 24" diameter |  | 0 | LF | 476 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Utilidor Rehabilitation and Repair
Repair and recondition utilidor walls, floor and removable roof panels; repair/replace utilidor insulation and waterproofing system. |  | 50 | LF | 125 | 6250 | 5% | 2% | 5% | 12.2% | 10% | 312.5 | 131.25 | 334.6875 | 857.4694 | 788.5907 | 8674.4976 | 5% | 5% | 5% | 10% | 433.7249 | 433.7249 | 433.7249 | 86.745 | 10062.4172 | 75 |  | 75
Raise elevation of manhole lid where required to eliminate seasonal flooding of utilidor system. |  | 4 | EA | 1750 | 7000 | 5% | 2% | 5% | 12.2% | 10% | 350 | 147 | 374.85 | 960.3657 | 883.2216 | 9715.4373 | 5% | 5% | 5% | 10% | 485.7719 | 485.7719 | 485.7719 | 97.1544 | 11269.9072 | 75 |  | 75
Repair/replace utilidor ventilation system in manhole lid (where required). |  | 4 | EA | 2200 | 8800 | 5% | 2% | 5% | 12.2% | 10% | 440 | 184.8 | 471.24 | 1207.3169 | 1110.3357 | 12213.6926 | 5% | 5% | 5% | 10% | 610.6846 | 610.6846 | 610.6846 | 122.1369 | 14167.8834 | 75 |  | 75
Replace manhole convenience power and lighting system (where required). |  | 4 | EA | 1800 | 7200 | 5% | 2% | 5% | 12.2% | 10% | 360 | 151.2 | 385.56 | 987.8047 | 908.4565 | 9993.0212 | 5% | 5% | 5% | 10% | 499.6511 | 499.6511 | 499.6511 | 99.9302 | 11591.9046 | 25 |  | 25
Replace utilidor drainage system , sump pumps (where required) |  | 0 | EA | 2600 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Replace existing access hatches with new secure (lockable) hatches. |  | 4 | EA | 3065 | 12260 | 5% | 2% | 5% | 12.2% | 10% | 613 | 257.46 | 656.523 | 1682.0119 | 1546.8995 | 17015.8944 | 5% | 5% | 5% | 10% | 850.7947 | 850.7947 | 850.7947 | 170.1589 | 19738.4375 | 75 |  | 75
Utilidor Replacement - Includes removal and recycling of existing concrete utilidor elements. Replacement also includes mastic damp proofing, board insulation, access hatches, vents, lighting, and sumps with submersible pumps.
8 foot long precast concrete U-sections with precast concrete lids; ACI 317, 5000 psi concrete,
Precast concrete sections - 84" by 108" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 84" |  | 0 | LF | 920 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 60" |  | 0 | LF | 789 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 48" |  | 0 | LF | 723 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 78" by 78" |  | 0 | LF | 862 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 84" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 72" |  | 0 | LF | 804 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 60" |  | 0 | LF | 738 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 36" |  | 0 | LF | 607 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 72" |  | 0 | LF | 754 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Precast concrete sections - 60" by 60" |  | 0 | LF | 688 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 48" |  | 0 | LF | 623 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 30" |  | 0 | LF | 524 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 54" by 60" |  | 0 | LF | 663 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 54" by 54" |  | 0 | LF | 630 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 48" by 60" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 48" by 48" |  | 0 | LF | 572 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 42" by 42" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 42" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 36" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 36" |  | 0 | LF | 410 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 24" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 48" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 24" |  | 400 | LF | 265 | 106000 | 5% | 2% | 5% | 12.2% | 10% | 5300 | 2226 | 5676.3 | 14542.6806 | 13374.4981 | 147119.4787 | 5% | 5% | 5% | 10% | 7355.9739 | 7355.9739 | 7355.9739 | 1471.1948 | 170658.5952 | 75 |  | 75
Precast concrete sections - 18" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 18" by 24" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Direct Buried Heat Distribution Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Class A conduit system, drainable, dryable, pressure testable. Standard weight steel pipe for steam; schedule 10S for condensate; foamglas insulation on carrier pipe; FRP coating as protection on conduit.
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 2" Steam & 1" Condensate |  | 0 | LF | 200 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 4" Steam & 1" Condensate |  | 0 | LF | 280 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 6" Steam & 2" Condensate |  | 0 | LF | 370 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 8" Steam & 4" Condensate |  | 0 | LF | 450 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main - 12" Steam & 6" Condensate |  | 0 | LF | 869 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried Domestic Water Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
direct buried water main (DU Water Service Table March 2008) - 4" diameter |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water main (DU Water Service Table March 2008) - 6" diameter |  | 100 | LF | 110 | 11000 | 5% | 2% | 5% | 12.2% | 10% | 550 | 231 | 589.05 | 1509.1461 | 1387.9196 | 15267.1157 | 5% | 5% | 5% | 10% | 763.3558 | 763.3558 | 763.3558 | 152.6712 | 17709.8542 | 70 |  | 70
direct buried water main (DU Water Service Table March 2008) - 8" diameter |  | 0 | LF | 120 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 10" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 14" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 16" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 18" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 20" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Direct Buried Sewer Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
Gravity:
direct buried sewer piping - 3" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 4" gravity |  | 0 | LF | 65 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 6" gravity |  | 0 | LF | 70 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 8" gravity |  | 375 | LF | 254 | 95250 | 5% | 2% | 5% | 12.2% | 10% | 4762.5 | 2000.25 | 5100.6375 | 13067.8333 | 12018.1221 | 132199.3429 | 5% | 5% | 5% | 10% | 6609.9671 | 6609.9671 | 6609.9671 | 1321.9934 | 153351.2377 | 70 |  | 70
direct buried sewer piping - 10" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 12" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 14" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 16" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 18" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 20" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 24" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Force Main:
direct buried sewer main (DU Sewer Service Table March 2008) - 4" force main |  | 0 | LF | 65 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 6" force main |  | 0 | LF | 70 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 8" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 10" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 12" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 14" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 16" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 18" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 20" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 24" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Other Project Specific Items
Replace condensate pump station |  | 0 | EA | 20000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 35 |  | 35
Fire hydrant - new including manhole, lateral piping, tracing and insulation |  | 0 | EA | 52250 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Fire hydrant - replacement including lateral piping, tracing and insulation |  | 2 | EA | 17500 | 35000 | 5% | 2% | 5% | 12.2% | 10% | 1750 | 735 | 1874.25 | 4801.8285 | 4416.1079 | 48577.1864 | 5% | 5% | 5% | 10% | 2428.8593 | 2428.8593 | 2428.8593 | 485.7719 | 56349.5362 | 25 |  | 25
Force main lift station - Bldg ? |  | 0 | EA | 120000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Water well station - Bldg ? |  | 0 | EA | 18000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Emergency repair of HDS pipe insulation including removal of existing ACM pipe insulation |  | 0 | LF | 400 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Total Project Cost |  |  |  |  | 615560 | [10 empty] | 854347.7951 | [5 empty] | Total CPM & Commissioning | 42717.3898 |  | 991043.4424 |  |  | 64.3525
[19 empty] | Total Pre-design, Design & Fees on Design | 51260.8677
[19 empty] | Total CPM & Commissioning | 42717.3898
416012.5256

## FTW336A Lat (14 Sep 09)
Project Cost Estimating Worksheet
Fort Wainwright FTW336A | Utility Service Lateral from Existing Mains to Aircraft Parts Storage
Item | Year Inst | Quantity |  | Unit Cost | RCN | Contractors Mark-ups % |  |  |  |  | Contractors Mark-ups $ |  |  |  |  | RCN (Total Installed) | Engineering Services % |  |  |  | Engineering Services $'s |  |  |  | RCN Total w. Engineering) | Design Life | RYN (Repl. Year New) | RDL (Repl. Design Life) | Comments
[6 empty] | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit |  | Studies & Pre-Design | Design | Services During Construction(3%) & Commissioning (2%) | Fee's on Studies & Design | Studies & Pre-Design | Design | Services During Construction | Fee's on Studies & Design |  |  | CY
FTW
Site Preparation & Access
site preparation, overburden excavation and removal, sedimentation control |  | 400 | LF | 50 | 20000 | 5% | 2% | 5% | 12.2% | 10% | 1000 | 420 | 1071 | 2743.902 | 2523.4902 | 27758.3922 | 5% | 5% | 5% | 10% | 1387.9196 | 1387.9196 | 1387.9196 | 277.5839 | 32199.735 | 75 |  | 75
isolation tenting, ventilation, lid removal and cribbing, isolation bulkheads, repair or replacement of broken utilidor roof panels |  | 0 | LF | 25 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
utilidor roof panel clean-up and reinstallation; backfill; finish grading; pavement repair; turf and landscape repair. |  | 400 | LF | 75 | 30000 | 5% | 2% | 5% | 12.2% | 10% | 1500 | 630 | 1606.5 | 4115.853 | 3785.2353 | 41637.5883 | 5% | 5% | 5% | 10% | 2081.8794 | 2081.8794 | 2081.8794 | 416.3759 | 48299.6024 | 75 |  | 75
Asbestos Containing Material Abatement
asbestos pipe insulation removal and disposal in POST landfill |  | 0 | LF | 175 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
utilidor clean up & asbestos encapsulation |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Utilidor Steam Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Carbon steel piping, ASTM A106, seamless, standard wall; forged carbon steel fittings; forged carbon steel valves (2" and smaller); cast carbon steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed steam piping - 1" diameter |  | 0 | LF | 161 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 1½" diameter |  | 0 | LF | 175 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 2" diameter |  | 0 | LF | 191 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 3" diameter |  | 400 | LF | 233 | 93200 | 5% | 2% | 5% | 12.2% | 10% | 4660 | 1957.2 | 4990.86 | 12786.5833 | 11759.4643 | 129354.1077 | 5% | 5% | 5% | 10% | 6467.7054 | 6467.7054 | 6467.7054 | 1293.5411 | 150050.7649 | 60 |  | 60
utilidor installed steam piping - 4" diameter |  | 0 | LF | 292 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 6" diameter |  | 0 | LF | 320 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 8" diameter |  | 0 | LF | 374 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 10" diameter |  | 0 | LF | 447 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 12" diameter |  | 0 | LF | 505 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 14" diameter |  | 0 | LF | 547 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 16" diameter |  | 0 | LF | 588 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 18" diameter |  | 0 | LF | 691 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 20" diameter |  | 0 | LF | 785 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 24" diameter |  | 0 | LF | 891 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
Utilidor Condensate Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Stainless steel piping, ASTM A312, Type 316L, schedule 10S; wrought stainless steel fittings; forged stainless steel valves (2" and smaller); cast stainless steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed condensate piping - ½" diameter |  | 0 | LF | 190 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - ¾" diameter |  | 0 | LF | 187 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 1" diameter |  | 0 | LF | 198 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 1½" diameter |  | 400 | LF | 205 | 82000 | 5% | 2% | 5% | 12.2% | 10% | 4100 | 1722 | 4391.1 | 11249.9982 | 10346.3098 | 113809.408 | 5% | 5% | 5% | 10% | 5690.4704 | 5690.4704 | 5690.4704 | 1138.0941 | 132018.9133 | 40 |  | 40
utilidor installed condensate piping - 2" diameter |  | 0 | LF | 217 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 3" diameter |  | 0 | LF | 230 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 4" diameter |  | 0 | LF | 250 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 6" diameter |  | 0 | LF | 364 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 8" diameter |  | 0 | LF | 350 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 10" diameter |  | 0 | LF | 401 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 12" diameter |  | 0 | LF | 423 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
Utilidor Water Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new support and anchor systems; new insulation and tracing; reconnect or replace service laterals as required.
Copper tubing (3" and smaller), ASTM B88, type K; cast bronze fittings, ASTM A536; cast bronze valves; mechanical couplings for roll grooved piping system.
utilidor installed water piping - 1½" diameter |  | 0 | LF | 54 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 2" diameter |  | 0 | LF | 63 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 2½" diameter |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 3" diameter |  | 0 | LF | 94 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
utilidor installed water piping - 4" diameter |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 6" diameter |  | 400 | LF | 221 | 88400 | 5% | 2% | 5% | 12.2% | 10% | 4420 | 1856.4 | 4733.82 | 12128.0468 | 11153.8267 | 122692.0935 | 5% | 5% | 5% | 10% | 6134.6047 | 6134.6047 | 6134.6047 | 1226.9209 | 142322.8285 | 70 |  | 70
utilidor installed water piping - 8" diameter |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 10" diameter |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 14" diameter |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 16" diameter |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 18" diameter |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 20" diameter |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Utilidor Sewer Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new support and anchor systems; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
Gravity:
utilidor installed sewer piping - 3" gravity |  | 0 | LF | 196 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 4" gravity |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 6" gravity |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 8" gravity |  | 400 | LF | 254 | 101600 | 5% | 2% | 5% | 12.2% | 10% | 5080 | 2133.6 | 5440.68 | 13939.0222 | 12819.3302 | 141012.6324 | 5% | 5% | 5% | 10% | 7050.6316 | 7050.6316 | 7050.6316 | 1410.1263 | 163574.6536 | 70 |  | 70
utilidor installed sewer piping - 10" gravity |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 12" gravity |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 14" gravity |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 16" gravity |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 18" gravity |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 20" gravity |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 24" gravity |  | 0 | LF | 476 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Force Main:
utilidor installed force main - 4" diameter |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 6" diameter |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 8" diameter |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 10" diameter |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 14" diameter |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 16" diameter |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 18" diameter |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 20" diameter |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 24" diameter |  | 0 | LF | 476 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Utilidor Rehabilitation and Repair
Repair and recondition utilidor walls, floor and removable roof panels; repair/replace utilidor insulation and waterproofing system. |  | 50 | LF | 125 | 6250 | 5% | 2% | 5% | 12.2% | 10% | 312.5 | 131.25 | 334.6875 | 857.4694 | 788.5907 | 8674.4976 | 5% | 5% | 5% | 10% | 433.7249 | 433.7249 | 433.7249 | 86.745 | 10062.4172 | 75 |  | 75
Raise elevation of manhole lid where required to eliminate seasonal flooding of utilidor system. |  | 1 | EA | 1750 | 1750 | 5% | 2% | 5% | 12.2% | 10% | 87.5 | 36.75 | 93.7125 | 240.0914 | 220.8054 | 2428.8593 | 5% | 5% | 5% | 10% | 121.443 | 121.443 | 121.443 | 24.2886 | 2817.4768 | 75 |  | 75
Repair/replace utilidor ventilation system in manhole lid (where required). |  | 0 | EA | 2200 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Replace manhole convenience power and lighting system (where required). |  | 0 | EA | 1800 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Replace utilidor drainage system , sump pumps (where required) |  | 0 | EA | 2600 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Replace existing access hatches with new secure (lockable) hatches. |  | 3 | EA | 3065 | 9195 | 5% | 2% | 5% | 12.2% | 10% | 459.75 | 193.095 | 492.3922 | 1261.5089 | 1160.1746 | 12761.9208 | 5% | 5% | 5% | 10% | 638.096 | 638.096 | 638.096 | 127.6192 | 14803.8281 | 75 |  | 75
Utilidor Replacement - Includes removal and recycling of existing concrete utilidor elements. Replacement also includes mastic damp proofing, board insulation, access hatches, vents, lighting, and sumps with submersible pumps.
8 foot long precast concrete U-sections with precast concrete lids; ACI 317, 5000 psi concrete,
Precast concrete sections - 84" by 108" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 84" |  | 0 | LF | 920 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 60" |  | 0 | LF | 789 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 48" |  | 0 | LF | 723 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 78" by 78" |  | 0 | LF | 862 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 84" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 72" |  | 0 | LF | 804 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 60" |  | 0 | LF | 738 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 36" |  | 0 | LF | 607 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 72" |  | 0 | LF | 754 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Precast concrete sections - 60" by 60" |  | 0 | LF | 688 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 48" |  | 0 | LF | 623 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 30" |  | 0 | LF | 524 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 54" by 60" |  | 0 | LF | 663 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 54" by 54" |  | 0 | LF | 630 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 48" by 60" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 48" by 48" |  | 0 | LF | 572 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 42" by 42" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 42" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 36" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 36" |  | 400 | LF | 410 | 164000 | 5% | 2% | 5% | 12.2% | 10% | 8200 | 3444 | 8782.2 | 22499.9964 | 20692.6196 | 227618.816 | 5% | 5% | 5% | 10% | 11380.9408 | 11380.9408 | 11380.9408 | 2276.1882 | 264037.8266 | 75 |  | 75
Precast concrete sections - 30" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 24" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 48" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 24" |  | 0 | LF | 265 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 18" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 18" by 24" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Direct Buried Heat Distribution Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Class A conduit system, drainable, dryable, pressure testable. Standard weight steel pipe for steam; schedule 10S for condensate; foamglas insulation on carrier pipe; FRP coating as protection on conduit.
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 2" Steam & 1" Condensate |  | 0 | LF | 200 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 4" Steam & 1" Condensate |  | 0 | LF | 280 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 6" Steam & 2" Condensate |  | 0 | LF | 370 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 8" Steam & 4" Condensate |  | 0 | LF | 450 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main - 12" Steam & 6" Condensate |  | 0 | LF | 869 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried Domestic Water Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
direct buried water main (DU Water Service Table March 2008) - 4" diameter |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water main (DU Water Service Table March 2008) - 6" diameter |  | 0 | LF | 110 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water main (DU Water Service Table March 2008) - 8" diameter |  | 0 | LF | 120 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 10" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 14" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 16" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 18" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 20" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Direct Buried Sewer Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
Gravity:
direct buried sewer piping - 3" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 4" gravity |  | 0 | LF | 65 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 6" gravity |  | 0 | LF | 70 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 8" gravity |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 10" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 12" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 14" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 16" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 18" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 20" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 24" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Force Main:
direct buried sewer main (DU Sewer Service Table March 2008) - 4" force main |  | 0 | LF | 65 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 6" force main |  | 0 | LF | 70 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 8" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 10" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 12" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 14" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 16" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 18" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 20" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 24" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Other Project Specific Items
Replace condensate pump station |  | 0 | EA | 20000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 35 |  | 35
Fire hydrant - new including manhole, lateral piping, tracing and insulation |  | 0 | EA | 52250 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Fire hydrant - replacement including lateral piping, tracing and insulation |  | 2 | EA | 17500 | 35000 | 5% | 2% | 5% | 12.2% | 10% | 1750 | 735 | 1874.25 | 4801.8285 | 4416.1079 | 48577.1864 | 5% | 5% | 5% | 10% | 2428.8593 | 2428.8593 | 2428.8593 | 485.7719 | 56349.5362 | 25 |  | 25
Force main lift station - Bldg ? |  | 0 | EA | 120000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Water well station - Bldg ? |  | 0 | EA | 18000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Emergency repair of HDS pipe insulation including removal of existing ACM pipe insulation |  | 0 | LF | 400 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Total Project Cost |  |  |  |  | 631395 | [10 empty] | 876325.5022 | [5 empty] | Total CPM & Commissioning | 43816.2751 |  | 1016537.5825 |  |  | 64.3525
[19 empty] | Total Pre-design, Design & Fees on Design | 52579.5301
[19 empty] | Total CPM & Commissioning | 43816.2751
441506.6658

## FTW336A Service Lateral
Project Cost Estimating Worksheet
Fort Wainwright FTW336A | Utility Service Lateral from Existing Mains to Aircraft Parts Storage
Item | Year Inst | Quantity |  | Unit Cost | RCN | Contractors Mark-ups % |  |  |  |  | Contractors Mark-ups $ |  |  |  |  | RCN (Total Installed) | Engineering Services % |  |  |  | Engineering Services $'s |  |  |  | RCN Total w. Engineering) | Design Life | RYN (Repl. Year New) | RDL (Repl. Design Life) | Comments
[6 empty] | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit | Contingency | Bonds & Insurance | General Conditions | Contractors G&A | Contractors Profit |  | Studies & Pre-Design | Design | Services During Construction(3%) & Commissioning (2%) | Fee's on Studies & Design | Studies & Pre-Design | Design | Services During Construction | Fee's on Studies & Design |  |  | CY
FTW
Site Preparation & Access
site preparation, overburden excavation and removal, sedimentation control |  | 475 | LF | 50 | 23750 | 5% | 2% | 5% | 12.2% | 10% | 1187.5 | 498.75 | 1271.8125 | 3258.3836 | 2996.6446 | 32963.0907 | 5% | 5% | 5% | 10% | 1648.1545 | 1648.1545 | 1648.1545 | 329.6309 | 38237.1853 | 75 |  | 75
isolation tenting, ventilation, lid removal and cribbing, isolation bulkheads, repair or replacement of broken utilidor roof panels |  | 0 | LF | 25 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
utilidor roof panel clean-up and reinstallation; backfill; finish grading; pavement repair; turf and landscape repair. |  | 475 | LF | 75 | 35625 | 5% | 2% | 5% | 12.2% | 10% | 1781.25 | 748.125 | 1907.7188 | 4887.5754 | 4494.9669 | 49444.6361 | 5% | 5% | 5% | 10% | 2472.2318 | 2472.2318 | 2472.2318 | 494.4464 | 57355.7779 | 75 |  | 75
Asbestos Containing Material Abatement
asbestos pipe insulation removal and disposal in POST landfill |  | 0 | LF | 175 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
utilidor clean up & asbestos encapsulation |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Utilidor Steam Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Carbon steel piping, ASTM A106, seamless, standard wall; forged carbon steel fittings; forged carbon steel valves (2" and smaller); cast carbon steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed steam piping - 1" diameter |  | 0 | LF | 161 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 1½" diameter |  | 0 | LF | 175 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 2" diameter |  | 0 | LF | 191 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 3" diameter |  | 300 | LF | 233 | 69900 | 5% | 2% | 5% | 12.2% | 10% | 3495 | 1467.9 | 3743.145 | 9589.9375 | 8819.5982 | 97015.5807 | 5% | 5% | 5% | 10% | 4850.779 | 4850.779 | 4850.779 | 970.1558 | 112538.0737 | 60 |  | 60
utilidor installed steam piping - 4" diameter |  | 0 | LF | 292 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 6" diameter |  | 0 | LF | 320 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 8" diameter |  | 0 | LF | 374 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 10" diameter |  | 0 | LF | 447 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 12" diameter |  | 0 | LF | 505 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 14" diameter |  | 0 | LF | 547 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 16" diameter |  | 0 | LF | 588 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 18" diameter |  | 0 | LF | 691 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 20" diameter |  | 0 | LF | 785 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
utilidor installed steam piping - 24" diameter |  | 0 | LF | 891 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 60 |  | 60
Utilidor Condensate Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new supports, expansion compensation and anchor systems; new insulation; reconnect or replace service laterals as required.
Stainless steel piping, ASTM A312, Type 316L, schedule 10S; wrought stainless steel fittings; forged stainless steel valves (2" and smaller); cast stainless steel valves (3" and larger); externally pressurized expansion joints; all welded piping system.
utilidor installed condensate piping - ½" diameter |  | 0 | LF | 190 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - ¾" diameter |  | 0 | LF | 187 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 1" diameter |  | 0 | LF | 198 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 1½" diameter |  | 300 | LF | 205 | 61500 | 5% | 2% | 5% | 12.2% | 10% | 3075 | 1291.5 | 3293.325 | 8437.4986 | 7759.7324 | 85357.056 | 5% | 5% | 5% | 10% | 4267.8528 | 4267.8528 | 4267.8528 | 853.5706 | 99014.185 | 40 |  | 40
utilidor installed condensate piping - 2" diameter |  | 0 | LF | 217 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 3" diameter |  | 0 | LF | 230 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 4" diameter |  | 0 | LF | 250 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 6" diameter |  | 0 | LF | 364 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 8" diameter |  | 0 | LF | 350 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 10" diameter |  | 0 | LF | 401 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
utilidor installed condensate piping - 12" diameter |  | 0 | LF | 423 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 40 |  | 40
Utilidor Water Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new support and anchor systems; new insulation and tracing; reconnect or replace service laterals as required.
Copper tubing (3" and smaller), ASTM B88, type K; cast bronze fittings, ASTM A536; cast bronze valves; mechanical couplings for roll grooved piping system.
utilidor installed water piping - 1½" diameter |  | 300 | LF | 54 | 16200 | 5% | 2% | 5% | 12.2% | 10% | 810 | 340.2 | 867.51 | 2222.5606 | 2044.0271 | 22484.2977 | 5% | 5% | 5% | 10% | 1124.2149 | 1124.2149 | 1124.2149 | 224.843 | 26081.7853 | 70 |  | 70
utilidor installed water piping - 2" diameter |  | 0 | LF | 63 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 2½" diameter |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 3" diameter |  | 0 | LF | 94 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
utilidor installed water piping - 4" diameter |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 6" diameter |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 8" diameter |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 10" diameter |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 14" diameter |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 16" diameter |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 18" diameter |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed water piping - 20" diameter |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Utilidor Sewer Piping System - includes demolition of existing pipes and supports; installation of new pipe; installation of new support and anchor systems; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
Gravity:
utilidor installed sewer piping - 3" gravity |  | 0 | LF | 196 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 4" gravity |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 6" gravity |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 8" gravity |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 10" gravity |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 12" gravity |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 14" gravity |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 16" gravity |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 18" gravity |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 20" gravity |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed sewer piping - 24" gravity |  | 0 | LF | 476 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Force Main:
utilidor installed force main - 4" diameter |  | 0 | LF | 207 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 6" diameter |  | 0 | LF | 221 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 8" diameter |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 10" diameter |  | 0 | LF | 263 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 14" diameter |  | 0 | LF | 316 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 16" diameter |  | 0 | LF | 345 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 18" diameter |  | 0 | LF | 387 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 20" diameter |  | 0 | LF | 422 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
utilidor installed force main - 24" diameter |  | 0 | LF | 476 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Utilidor Rehabilitation and Repair
Repair and recondition utilidor walls, floor and removable roof panels; repair/replace utilidor insulation and waterproofing system. |  | 50 | LF | 125 | 6250 | 5% | 2% | 5% | 12.2% | 10% | 312.5 | 131.25 | 334.6875 | 857.4694 | 788.5907 | 8674.4976 | 5% | 5% | 5% | 10% | 433.7249 | 433.7249 | 433.7249 | 86.745 | 10062.4172 | 75 |  | 75
Raise elevation of manhole lid where required to eliminate seasonal flooding of utilidor system. |  | 1 | EA | 1750 | 1750 | 5% | 2% | 5% | 12.2% | 10% | 87.5 | 36.75 | 93.7125 | 240.0914 | 220.8054 | 2428.8593 | 5% | 5% | 5% | 10% | 121.443 | 121.443 | 121.443 | 24.2886 | 2817.4768 | 75 |  | 75
Repair/replace utilidor ventilation system in manhole lid (where required). |  | 0 | EA | 2200 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Replace manhole convenience power and lighting system (where required). |  | 0 | EA | 1800 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Replace utilidor drainage system , sump pumps (where required) |  | 0 | EA | 2600 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Replace existing access hatches with new secure (lockable) hatches. |  | 1 | EA | 3065 | 3065 | 5% | 2% | 5% | 12.2% | 10% | 153.25 | 64.365 | 164.1308 | 420.503 | 386.7249 | 4253.9736 | 5% | 5% | 5% | 10% | 212.6987 | 212.6987 | 212.6987 | 42.5397 | 4934.6094 | 75 |  | 75
Utilidor Replacement - Includes removal and recycling of existing concrete utilidor elements. Replacement also includes mastic damp proofing, board insulation, access hatches, vents, lighting, and sumps with submersible pumps.
8 foot long precast concrete U-sections with precast concrete lids; ACI 317, 5000 psi concrete,
Precast concrete sections - 84" by 108" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 84" |  | 0 | LF | 920 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 60" |  | 0 | LF | 789 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 84" by 48" |  | 0 | LF | 723 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 78" by 78" |  | 0 | LF | 862 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 84" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 72" |  | 0 | LF | 804 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 60" |  | 0 | LF | 738 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 72" by 36" |  | 0 | LF | 607 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 72" |  | 0 | LF | 754 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Precast concrete sections - 60" by 60" |  | 0 | LF | 688 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 48" |  | 0 | LF | 623 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 60" by 30" |  | 0 | LF | 524 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 54" by 60" |  | 0 | LF | 663 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 54" by 54" |  | 0 | LF | 630 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 48" by 60" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 48" by 48" |  | 0 | LF | 572 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 42" by 42" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 42" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 36" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 36" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 36" |  | 0 | LF | 410 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 30" by 24" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 48" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 24" by 24" |  | 275 | LF | 265 | 72875 | 5% | 2% | 5% | 12.2% | 10% | 3643.75 | 1530.375 | 3902.4563 | 9998.0929 | 9194.9674 | 101144.6416 | 5% | 5% | 5% | 10% | 5057.2321 | 5057.2321 | 5057.2321 | 1011.4464 | 117327.7842 | 75 |  | 75
Precast concrete sections - 18" by 30" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Precast concrete sections - 18" by 24" |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 75 |  | 75
Direct Buried Heat Distribution Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Class A conduit system, drainable, dryable, pressure testable. Standard weight steel pipe for steam; schedule 10S for condensate; foamglas insulation on carrier pipe; FRP coating as protection on conduit.
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 2" Steam & 1" Condensate |  | 0 | LF | 200 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 4" Steam & 1" Condensate |  | 0 | LF | 280 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 6" Steam & 2" Condensate |  | 0 | LF | 370 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main (DU Steam Heat Service Table March 2008) - 8" Steam & 4" Condensate |  | 0 | LF | 450 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried HDS Main - 12" Steam & 6" Condensate |  | 0 | LF | 869 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 30 |  | 30
Direct Buried Domestic Water Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
direct buried water main (DU Water Service Table March 2008) - 4" diameter |  | 0 | LF | 75 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water main (DU Water Service Table March 2008) - 6" diameter |  | 0 | LF | 110 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water main (DU Water Service Table March 2008) - 8" diameter |  | 0 | LF | 120 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 10" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 12" diameter |  | 0 | LF | 291 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 14" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 16" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 18" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried water piping - 20" diameter |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Direct Buried Sewer Piping System - includes demolition of existing pipes; installation of new pipe; installation of new support / anchor system; reconnect or replace service laterals as required.
Ductile iron piping (4" and larger), AWWA C151/A21.51, Class 53; cement lined, AWWA C104, standard; ductile iron fittings, ASTM A536; ductile iron valves; mechanical couplings for cut grooved and shouldered piping systems, AWWA C606.
Gravity:
direct buried sewer piping - 3" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 4" gravity |  | 0 | LF | 65 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 6" gravity |  | 200 | LF | 70 | 14000 | 5% | 2% | 5% | 12.2% | 10% | 700 | 294 | 749.7 | 1920.7314 | 1766.4431 | 19430.8745 | 5% | 5% | 5% | 10% | 971.5437 | 971.5437 | 971.5437 | 194.3087 | 22539.8145 | 70 |  | 70
direct buried sewer piping - 8" gravity |  | 0 | LF | 254 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 10" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 12" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 14" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 16" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 18" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 20" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 24" gravity |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Force Main:
direct buried sewer main (DU Sewer Service Table March 2008) - 4" force main |  | 0 | LF | 65 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer main (DU Sewer Service Table March 2008) - 6" force main |  | 0 | LF | 70 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 8" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 10" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 12" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 14" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 16" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 18" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 20" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
direct buried sewer piping - 24" force main |  | 0 | LF |  | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 70 |  | 70
Other Project Specific Items
Replace condensate pump station |  | 0 | EA | 20000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 35 |  | 35
Fire hydrant - new including manhole, lateral piping, tracing and insulation |  | 1 | EA | 52250 | 52250 | 5% | 2% | 5% | 12.2% | 10% | 2612.5 | 1097.25 | 2797.9875 | 7168.444 | 6592.6181 | 72518.7996 | 5% | 5% | 5% | 10% | 3625.94 | 3625.94 | 3625.94 | 725.188 | 84121.8076 | 75 |  | 75
Fire hydrant - replacement including lateral piping, tracing and insulation |  | 0 | EA | 17500 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Force main lift station - Bldg ? |  | 0 | EA | 120000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Water well station - Bldg ? |  | 0 | EA | 18000 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Emergency repair of HDS pipe insulation including removal of existing ACM pipe insulation |  | 0 | LF | 400 | 0 | 5% | 2% | 5% | 12.2% | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 5% | 5% | 10% | 0 | 0 | 0 | 0 | 0 | 25 |  | 25
Total Project Cost |  |  |  |  | 357165 | [10 empty] | 495716.3075 | [5 empty] | Total CPM & Commissioning | 24785.8154 |  | 575030.9167 |  |  | 64.3525
[19 empty] | Total Pre-design, Design & Fees on Design | 29742.9785
[19 empty] | Total CPM & Commissioning | 24785.8154